## Hi wall
Operation lamp | Timer lamp | IDU dispaly Code | 120 Wired controller display code | Meaning of Troubles
☆ 1 time | X | EH 00/EH 0R | E7 | Indoor unit EEPROM parameter error
☆ 2 times | X | EL 01 | E1 | Indoor / outdoor units communication error
☆ 3 times | X | EH 02 | E6 | Zero-crossing signal detection error (Not available for DC indoor fan motor)
☆ 4 times | X | EH 03 | E8 | Indoor fan speed has been out of control
☆ 6 times | X | EH 60 | E2 | Indoor room temperature sensor T1 open circuit or short circuit
☆ 6 times | X | EH 61 | E4 | Evaporator coil temperature sensor T2 open circuit or short circuit
☆ 8 times | X | EL 0C |  | Refrigerant leakage detection
☆ 9 times | X | EH 0b | E9 | Communication error between indoor PCB and display PCB
☆ 5 times | X | EC 53 | E5 | Outdoor ambient temperature sensor T4 open circuit or short circuit
☆ 5 times | X | EC 52 | E5 | Condenser coil temperature sensor T3 open circuit or short circuit
☆ 5 times | X | EC 54 | E5 | Compressor discharge temperature sensor T5 open circuit or short circuit
☆ 5 times | X | EC 51 | N/A | Outdoor unit EEPROM parameter error
☆ 12 times | X | EC 07 | N/A | Outdoor fan speed has been out of control (DC fan motor only)
☆ 7 times | ☆ | PC 00 | EB | IPM malfunction or IGBT over-strong current protection
☆ 2 times | ☆ | PC 01 | N/A | DC voltage between P&N out of range
☆ 3 times | ☆ | PC 02 | N/A | High temperature protection of IPM module or High pressure protection(for some models)
☆ 5 times | ☆ | PC 04 | N/A | Inverter compressor drive error
☆ 1 times | ☆ | PC 08 | P8 | Over-current protection
☆ 6 times | ☆ | PC 40 | N/A | Communication error between outdoor chip and compressor drive chip
☆7 times | ☆ | PC 03 | N/A | Pressure protection or Outdoor ambient temperature is too low
|  | -- -- | N/A | Mode conflict
|  | N/A | F0 | Communication error between wired controller and indoor unit
|  | N/A | F1 | The cassette faceplate is abnormal
|  | N/A | EF | Other fault
|  | N/A | EC | Air clean malfuction
|  | N/A | E0 | Phase sequence error or phase malfuction
|  | N/A | PF | Other Protection
|  | N/A | EE | Full-water malfuction
|  | N/A | ED | Outdoor malfuction protection
|  | N/A | EC | Air clean malfuction
|  | N/A | EA | Compressor overload (4 times)
|  | N/A | PF | Other Protection
|  | N/A | P7 | Over-voltage protectionion
|  | N/A | P6 | Discharge low pressure protection
|  | N/A | P5 | Discharge high pressure protection
|  | N/A | P4 | Discharge pige termperature protection
|  | N/A | P3 | Compressor termperature protection
|  | N/A | P2 | Condensor termperature protection
|  | N/A | P1 | Enter anti-code or defrost mode
|  | N/A | P0 | Evaporator termperature protection