## Tester and Test board
Tester and Test board display error code
Error Code | Explanation
E0 | Indoor EEPROM error
E1 | Communication error of indoor and outdoor unit
E2 | Error of zero cross detection of indoor unit
E3 | Indoor fan out of control
E5 | EERROM or temperature sensor error of outdoor unit
E50 | Temperature sensor error of outdoor unit
E51 | Outdoor EEPROM error
E6 | Temperature sensor error of indoor unit
E60 | Error of room temperature sensor of indoor unit
E61 | Error of evaporator temperature sensor of indoor unit
E7 | DC fan of outdoor unit out of control
Eb | Error of communication between indoor PCB and display PCB
P0 | IPM Module protection of outdoor unit
P1 | Voltage protection
P10 | Low voltage low protection
P11 | Over voltage protection
P12 | Error of 341MCE
P2 | Top temperature protection of compressor
P4 | Feedback protection of compressor in outdoor unit
P40 | Communication error between main control trip and drive chip
P41 | Error of current sampling circuit of compressor
P42 | Error of compressor start up
P43 | Phase lose protection
P44 | Zero speed protection
P45 | Synchronization error between 341 chip and PWM
P46 | Compressor speed out of control
P49 | Error of over current of compressor
P6 | High discharge temperature protection of compressor
P8 | Current protection
P80 | Current protection of indoor unit
P81 | Current protection of outdoor unit
P82 | Error of sampling of input AC
P9 | High and low temperature protection of evaporator
P90 | High temperature protection of evaporator
P91 | Low temperature protection of evaporator
PA | High temperature protection of condenser
L0 | Frequency limit caused by High or low evaporator temperature
L1 | Frequency limit caused by high condenser temperature
L2 | Frequency limit caused by high discharge temperature of compressor
L3 | Frequency limit caused by current
L5 | Frequency limit caused by voltage
PF | PFC circuit error

## Engineer mode
Detailed Error Code (2 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
P10 | Low DC voltage protection | Outdoor PCB or IPM board | P1
P11 | High DC voltage protection | Outdoor PCB or IPM board | P1
P40 | Communication error between main control trip and drive chip | Outdoor PCB or IPM board | P4
P41 | Error of current sampling circuit of compressor | Outdoor PCB or IPM board | P4
P42 | Error of compressor start up | Compressor | P4
P43 | Phase lose protection | Connection cable of compressor | P4
P44 | Zero speed protection | Compressor | P4
P45 | Synchronization error between 341 chip and PWM | Outdoor PCB or IPM board | P4
P46 | Compressor speed out of control | Outdoor PCB or IPM board, or compressor | P4
P49 | Over current of compressor | Outdoor PCB or IPM board, compressor or refrigeration system | P4
Detailed Error Code (4 digits)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
P10 | Low DC voltage protection | Outdoor PCB or IPM board | P1
P11 | High DC voltage protection | Outdoor PCB or IPM board | P1
P40 | Communication error between main control trip and drive chip | Outdoor PCB or IPM board | P4
P41 | Error of current sampling circuit of compressor | Outdoor PCB or IPM board | P4
P42 | Error of compressor start up | Compressor | P4
P43 | Phase lose protection | Connection cable of compressor | P4
P44 | Zero speed protection | Compressor | P4
P45 | Synchronization error between 341 chip and PWM | Outdoor PCB or IPM board | P4
P46 | Compressor speed out of control | Outdoor PCB or IPM board, or compressor | P4
P49 | Over current of compressor | Outdoor PCB or IPM board, compressor or refrigeration system | P4
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
EH 31 | DC voltage is too low of indoor DC fan motor (with DC fan driver board) | Indoor PCB or DC fan driver board | EH 03
EH 32 | DC voltage is too high of indoor DC fan motor (with DC fan driver board) | Indoor PCB or DC fan driver board | EH 03
EH 33 | Over-current protection of indoor DC fan motor (with DC fan driver board) | Indoor PCB, DC fan driver board or indoor DC motor | EH 03
EH 34 | IPM protection of indoor DC fan motor (with DC fan driver board) | DC fan driver board or indoor DC motor | EH 03
EH 35 | Phase lack protection of indoor DC fan motor (with DC fan driver board) | Connection cable of indoor DC motor | EH 03
EH 36 | Current checking circuit faulty of indoor DC fan motor (with DC fan driver board) | DC fan driver board | EH 03
EH 37 | Zero speed protection of indoor DC fan motor (with DC fan driver board) | Indoor DC motor | EH 03
EC 55 | IPM temperature sensor open circuit or short circuit | IPM temperature sensor | EC 02
EC 71 | Over-current protection of outdoor DC fan motor | Outdoor PCB or DC motor | EC 07
EC 72 | Phase lack protection of outdoor DC fan motor | Connection cable of outdoor DC motor | EC 07
EC 73 | Zero speed protection of outdoor DC fan motor | Outdoor DC motor | EC 07
EC 74 | Current checking circuit faulty of outdoor DC fan motor | Outdoor PCB | EC 07
EC 75 | IPM protection of outdoor DC fan motor | Outdoor PCB or DC motor | EC 07
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
EH b5 | Communication error between indoor PCB and smart eye | Indoor PCB or smart eye | EH 03
EH 0F | Smart eye fault | Smart eye | EH 03
EH 0L | Display EEPROM fault | Display board | EH 0b
PC 10 | Outdoor AC voltage is too low | Power supply or outdoor PCB | PC 01
PC 11 | Outdoor DC voltage is too high | Power supply or outdoor PCB | PC 01
PC 12 | Outdoor DC voltage is too low (MCE faulty of IR341 chip) | Power supply or outdoor PCB (Outdoor PCB) | PC 01
PC 40 | Communication error between main control trip and drive chip | Outdoor PCB or IPM board | PC 04
PC 41 | Error of current sampling circuit of compressor | Outdoor PCB or IPM board | PC 04
PC 42 | Error of compressor start up | Compressor | PC 04
PC 43 | Phase lose protection | Connection cable of compressor | PC 04
PC 44 | Zero speed protection | Compressor | PC 04
PC 45 | Suddenly power lost | Power wire looses connection | PC 04
PC 46 | Compressor speed out of control | Outdoor PCB or IPM board, or compressor | PC 04
PC 49 | Over current of compressor | Outdoor PCB or IPM board, compressor or refrigeration system | PC 04
PC 06 | High discharge temperature protection of compressor | Lack of refrigerant, blocked condenser (cooling) or blocked evaporator (heating)
Detailed Code | Meaning | Possible Faulty Part | Normal Error Code
PC 08 | Over current of outdoor unit | Power supply, outdoor PCB or blocked refrigeration system
PH 09 | Indoor fan stop because of anti-cold wind function | Lack of refrigerant or blocked refrigeration system
PC 0F | IGBT fault of PFC circuit | Outdoor PCB
PH 90 | Hi evaporator temperature protection in heating mode | Blocked evaporator or capillary, EXV, or faulty sensor
PH 91 | Lo evaporator temperature protection in cooling mode | Lack of refrigerant or partial blocked capillary, EXV, or faulty sensor
PC 0A | Hi condenser temperature protection in cooling mode | Blocked condenser or capillary, EXV, or faulty sensor
LH 00 | Frequency limitation caused by high or low evaporator temperature
LC 01 | Frequency limitation caused by high condenser temperature
LC 02 | Frequency limitation caused by high discharge temperature
LC 03 | Frequency limitation caused by high current
LC 05 | Frequency limitation caused by high or low voltage
LC 06 | Frequency limitation caused by high IPM temperature or faulty PFC
LC 30 | Frequency limitation caused by high pressure
LC 31 | Frequency limitation caused by low pressure
LH 07 | Frequency limitation caused remote controller

## Multi CDU
Multi outdoor unit error code explanation
Detailed Error Code (2 digits)
E0 | Outdoor EEPROM malfunction
E2 | Indoor / outdoor units communication error
E3 | Communication malfunction between IPM board and outdoor main board
E4 | Open or short circuit of outdoor unit temperature sensor(T3,T4.T5)
E5 | Voltage protection
E6 | PFC module protection
E8 | Outdoor fan speed has been out of control or compressor speed has been out of control
F1 | No A Indoor unit coil outlet temperature sensor or connector of sensor is defective
F2 | No B Indoor unit coil outlet temperature sensor or connector of sensor is defective
F3 | No C Indoor unit coil outlet temperature sensor or connector of sensor is defective
F4 | No D Indoor unit coil outlet temperature sensor or connector of sensor is defective
F5 | No E Indoor unit coil outlet temperature sensor or connector of sensor is defective
P0 | Top temperature protection of compressor
P1 | High pressure protection (For M4OB-36HFN8-Q, M5OD-42HFN8-Q)
P2 | Low pressure protection (For M4OB-36HFN8-Q, M5OD-42HFN8-Q)
P3 | Current protection of compressor
P4 | Temperature protection of compressor discharge
P5 | High temperature protection of condenser
P6 | IPM module protection
E9 | 24k indoor unit wiring error
LP | Low ambient temperature protection
Note: Once these error codes display, they will disappear in at least 30 seconds if the unit come back to normal.(Except E2&E3)
Detailed Error Code 4( digits)
EC 51 | Outdoor EEPROM malfunction
EL 01 | Indoor / outdoor units communication error
PC 40 | Communication malfunction between IPM board and outdoor main board
PC 08 | Outdoor overcurrent protection
PC 1 0 | Outdoor unit low AC voltage protection
PC 11 | Outdoor unit main control board DC bus high voltage protection
PC 12 | Outdoor unit main control board DC bus high voltage protection /341 MCE error
PC 00 | IPM module protection
PC 0F | PFC module protection
EC 71 | Over current failure of outdoor DC fan motor
EC 72 | Lack phase failure of outdoor DC fan motor
EC 07 | Outdoor fan speed has been out of control
PC 43 | Outdoor compressor lack phase protection
PC 44 | Outdoor unit zero speed protection
PC 45 | Outdoor unit IR chip drive failure
PC 46 | Compressor speed has been out of control
PC 49 | Compressor overcurrent failure
PC 30 | High pressure protection (For 42K)
PC 31 | Low pressure protection (For 42K)
PC 0A | High temperature protection of condenser
PC 06 | Temperature protection of compressor discharge
PC 0L | Low ambient temperature protection
PC 02 | Top temperature protection of compressor
EC 52 | Condenser coil temperature sensor T3 is in open circuit or has short circuited
EC 53 | Outdoor room temperature sensor T4 is in open circuit or has short circuited
EC 54 | Compressor discharge temperature sensor T5 is in open circuit or has short circuited
EC 56 | Evaporator coil outlet temperature sensor T2B is in open circuit or has short circuited
EC 50 | Open or short circuit of outdoor unit temperature sensor(T3,T4.T5)